## TestRecords
Record Ref | Equipment ID | Work Order | Test Type | Reading | Unit | Result | Comments | Technician | Test Date
TR-0001 | P-101 | WO-2201 | Insulation Resistance | 520 | MΩ | Pass | Motor windings to earth, 500 V test | khengyee.goh@inferlens.com | 2026-09-15
TR-0002 | M-201 | WO-2205 | Vibration | 3.2 | mm/s | Pass | Drive end bearing | you@yourcompany.com | 2026-09-17
TR-0003 | TX-301 | WO-2207 | Temperature | 78 | °C | Conditional | Top oil temp high-ish, recheck next week | siti.noor@yourcompany.com | 2026-09-18
TR-0004 | PG-501 | WO-2210 | Calibration Check | 1.8 | % error | Fail | Outside tolerance, gauge tagged for replacement | you@yourcompany.com | 2026-09-22
TR-0005 | DB-602 | WO-2212 | Earth Continuity | 0.12 | Ω | Pass |  | aiman.rahman@yourcompany.com | 2026-09-24